# INDUSTRIAL CONTROL PANELS, (NITW, NITW7) - UL508A

# FOLLOW-UP AND INSPECTION INSTRUCTIONS

COPYRIGHT © 2022 UL LLC

TABLE OF CONTENTS

SCOPE	1

GENERAL	4

GENERAL RESPONSIBILITIES OF THE MANUFACTURER AND THE FIELD ENGINEER	4

GENERAL INSPECTION GUIDELINES	5

APPLICATION OF THE LISTING MARK TO THE PRODUCT	5

L1 Sample Products:	5

L2 Certification Mark Requirements:	5

L3 Listee Name:	5

L4 Mark Applied:	5

L5 Listing Marks:	5

FIELD ENGINEER’S COUNTERCHECK PROGRAM	6

L6 Inspection Instructions:	6

L7 Manufacturers’ Test Program:	6

INDUSTRIAL CONTROL PANEL ENCLOSURES	6

L8 Panel Enclosure:	6

L9 Enclosure Openings:	6

L10 Markings:	6

COMPONENTS	6

L11 Category Control Number:	6

L12 Procedure Description:	7

L13 Industrial Use:	7

L14 Listed Components:	7

L15 Recognized Components:	7

L16 New/Rebuilt:	7

L17 Other NRTL Components:	7

L18 Canadian Certification:	20

L19 Optional Components:	25

CONSTRUCTION	25

L20 General:	25

L21 Spacings:	25

L22 Spacings Between Components:	26

L23 Grounding and Bonding:	26

L24 Power Supply Grounding:	26

L25 Slash Voltage Grounding:	26

ENCLOSURE	26

L26 General Enclosure:	26

L27 Enclosure Type Ratings:	26

L28 Component Type Ratings:	26

L29 Arcing Parts Spacings:	27

POWER CIRCUITS	27

L30 General:	27

L31 Field Wiring:	27

L32 Multiple Conductors:	27

L33 Internal Wiring:	27

L34 Class B and C Conductors:	27

L35 Flexible Conductors:	27

L36 Multiple Conductor Termination:	28

L37 Flexible Bus Bar:	28

L38 Disconnecting Means:	28

L39 Combination Motor Controllers:	28

L40 Branch Circuit Protection:	28

L41 For Future Use:	28

L42 Branch Circuit Protection of Motor Groups:	28

L43 Feeder Taps for Motor Loads:	28

L44 Overcurrent Protection of Feeder:	29

L45 Load Controllers:	29

L46 Motor Overload Protection:	29

L47 Power Transformer:	29

CONTROL CIRCUITS	29

L48 General:	29

L49 Field Wiring:	29

L50 Internal Wiring:	29

L51 Conductor Sizing Greater Than 10 Amps:	29

L52 Overcurrent Protection:	29

L53 Overcurrent Protection for Grounded Conductor:	29

L54 Switching Devices:	29

L55 Loads:	29

RATINGS	29

L56 General:	30

L57 Short Circuit Current Ratings:	30

L58 Combination Motor Controllers:	30

L59 Series Connected Circuit Breakers:	30

L60 Maximum Ambient Temperature:	30

L61 Maximum Pneumatic Pressure Rating:	30

MARKINGS	30

L62 General:	30

L63 Reserved	30

L64 Enclosure Type Rating:	31

L65 Schematic Wiring Diagram:	31

L66 Hazardous Locations:	31

L67 Fountain Control Panels:	31

L68 Gas Detection Panels:	31

L69 Access Control Systems:	31

SPECIFIC USE INDUSTRIAL CONTROL PANELS	31

L70 General:	31

L71 Service Equipment:	31

L72 Reserved	32

L73 Flame Control:	32

L74 Fountain Control:	32

L75 Crane or Hoist Control:	32

L76 Air Conditioning and/or Refrigeration Control:	32

L77 Marine Use:	32

L78 Industrial Machinery:	32

L79 Aquatic Playground Control:	33

L80 Swimming Pool Control:	33

L81 Water Park Ride Control:	33

L82 Irrigation Control:	33

MANUFACTURER’S TEST PROGRAM	33

L83 General:	33

L84 Pass/Fail:	33

# SCOPE

A. These requirements cover industrial control panel enclosures, open industrial control panels and enclosed industrial control panels. Industrial control panels are evaluated to the requirements for one or more of the following:

- For general use;

- For use with industrial machinery (see L78);

- Reserved;

- As flame control panels (see L73);

- For service equipment use (see L71);

- As crane or hoist control panels (see L75);

- For use with air conditioning/refrigeration equipment (see L76);

- For marine use (see L77);

- As fountain control panels see L74);

- For use with irrigation equipment (see L82);

- For aquatic playgrounds (see L79);

- For swimming pools and In-ground spas (see L80); and

- For water park rides and similar installations (see L81).

B. These requirements do not cover any panel that is specifically covered under another UL standard in addition to:

- Fire pump controllers, controllers intended for starting and stopping centrifugal fire pumps, including automatic and non-automatic types for electric motor or engine driven pumps. Fire pump controllers are evaluated to UL218, are covered under category “Pump Controllers, Fire” (QYZS) and are intended to be installed in accordance with Article 695 of the National Electrical Code.  (Note: This does not exclude control panels for operating “jockey” or make-up pumps which serve to maintain water pressure in the system under normal, non-emergency conditions);

- Industrial control panels for use in hazardous (classified) locations, see L66, including controllers installed in:

- An explosion-proof or flame-proof enclosure marked for Class I hazardous locations or marked Type 7;

- A dust-ignition-proof enclosure marked for Class II hazardous locations or marked Type 9;

- Enclosed controllers provided with Listed purge and pressurization units marked for use in Class I or Class II hazardous locations; or

- Controllers utilizing non incendive circuits or devices and marked for use in Class I or II, Division 2 or Zone 2 hazardous locations.

Such equipment is evaluated to UL698, UL1203, UL1604, ISA-12.12.01, NFPA496 or the UL60079 series of standards as appropriate. They are covered under the categories “Control Panels and Assemblies for use in Hazardous Locations” (NNNY) or “Control Panels and Assemblies for use in Class I, Zone 0, 1 and 2 Hazardous Locations” (NWFA) and are intended to be installed in accordance with Article 500, 501, 502, or 505 of the National Electrical Code;

- Industrial control panels with intrinsically safe circuits that extend into a hazardous (classified) location (i.e. the control panel is intended for installation in an unclassified (ordinary) location but contains one or more devices intended to provide an intrinsically safe circuit, such as shunt – diode barriers, transformer isolated barriers, galvanically isolated barriers, etc.), see L66. Such equipment is evaluated to UL698A, are covered under the category “Industrial Control Panels Relating to Hazardous Locations” (NRBX) and are intended to be installed in accordance with Article 504 of the National Electrical Code;

- Pre-fabricated (walk-in or climb-in) buildings for installation above or below grade, structures or platforms for support of persons. Prefabricated buildings are classified for compliance with the National Electrical Code (and may additionally be evaluated to municipal building codes) and are covered under category “Commercial and Industrial Buildings” (QRNZ);

- Controls for swimming pools or spas mounted within 5 feet of the inside walls of the pool or spa, and control panels intended for use with equipment for water-play fountains, water-play areas, and fountains with water in common with swimming pools, including control panels containing swimming pool transformers, or that supply power to equipment in contact with water for such areas, such as submersible pumps, wet-niche or no-niche lighting fixtures, heaters, covers, chlorinators, and timers. See L80. Such equipment is evaluated to UL1563, are covered under category “Controls” (WAWU) and are intended to be installed in accordance with Article 680 of the National Electrical Code;

- Control equipment intended to supply automatic illumination, power, or both, to critical areas and equipment essential to safety of human life, including emergency lighting and power equipment. Such equipment is evaluated to the requirements contained in UL924, are covered under category “Emergency Lighting and Power Equipment” (FTBR) and intended for installation in accordance with Article 700 of the National Electrical Code;

- Fire alarm equipment, (including releasing equipment control units, and smoke control system equipment) and control panels containing electric control units for use in fire-protective signaling systems, or containing or having connections to smoke detectors, fire alarms and central station alarms, see L68. Such equipment or assemblies of equipment are evaluated to the requirements in UL864 and covered under “Control Units, Releasing Devices” (SYZV), “Control Units, System” (UOJZ), or “Smoke Control System Equipment”(UUKL;

- Gas or vapor detection equipment intended for connection to emergency alarm equipment, and emergency alarm control equipment containing or having connections to sensors or initiating devices to monitor, detect harmful concentrations of a gas or vapor (such as carbon monoxide (CO), carbon dioxide (CO2), or refrigerants) and/or activate emergency alarm equipment for life safety evacuation purposes, see L68. Such equipment or assemblies of equipment containing these devices is evaluated to UL2075 and covered under category “Gas and Vapor Detectors and Sensors” (FTAM), or evaluated to UL2017 and covered under the category “Emergency Alarm System Control Units” (FSZI) or “Emergency Alarm System Accessories” (FSYE);

- Termination boxes or enclosed assemblies consisting only of lengths of bus bars, terminal strips, or terminal blocks with provisions for wire connectors to accommodate conductors of power or distribution circuits. Such equipment is evaluated to the requirements in UL1773 and are covered under the category “Termination Boxes” (XCKT);

- Portable power distribution equipment, (consisting of plug and receptacle connections for input and outputs, power distribution only, no control circuit) for construction sites, theaters, motion picture and television studios, carnivals, circuses, fairs and exhibition halls. Such equipment is evaluated to the requirements in UL1640 and are covered under the category “Portable Power Distribution Units and Devices” (QPSH) or “Portable Power Distribution Panels” (QPSM) and are intended for installation in accordance with Articles 518, 520, 525, 530 or 590 of the National Electrical Code;

- The controlled equipment supplied from an industrial control panel, such as heaters, luminaries, motors, pumps, machines, robots, air conditioners, or other utilization equipment  (except for devices covered by Section 26 and Section 27 of the Standard that serve to condition air within the control panel itself or illumination of the interior of the control panel for servicing purposes);

- Motor control centers, including motor control center sections, motor control center units, or equipment mounted within motor control centers, which are constructed in one or more freestanding enclosed sections that are supplied with horizontal bus bars that serves as power connection between adjacent sections and having means to accommodate one or more plug-in or bolt-in motor control center units that are for control of motor loads. Such equipment is evaluated to the requirements contained in UL845 and are covered under the category “Motor Control Centers” (NJAV);

- Dead-front switchboards or equipment mounted within dead –front switchboards, which are constructed in one or more freestanding enclosed sections that predominantly contain bus bars and circuit breakers for control of electric power and lighting circuits. Such equipment is evaluated to the requirements contained in UL891, are covered under the category “Switchboards, Dead-Front” (WEVZ), and are intended for installation in accordance with Article 408 of the National Electrical Code; Control units for utility interactive systems (including distributed generation power systems, static converters and inverters for independent power systems, and photovoltaic power units);

- Control units for utility interactive systems (including distributed generation power systems, static converters and inverters for independent power systems (such as generators and fuel cells), and photovoltaic power units) and associated control devices and circuits that direct the operation of utility interactive systems. Such equipment is evaluated to the requirements in UL1741 and are covered under the categories of AC Modules (QHYZ), Distributed Resource Power Systems (QIJL) or Static Inverters and Converters for Use in Independent Power Systems (QIKH);

- Enclosures for communications equipment, including enclosure and rack systems, and power distribution centers, consisting of components, (such as switches, fuses, circuit breakers, power supplies, environmental control equipment such as fans, heaters, air conditioners or heat exchangers) to supply power, heat, cooling or otherwise support information technology (IT), telecommunications equipment, or audio/video equipment that is factory or field installed into open mounting panel or rack space. Such equipment is covered under the category “Information Technology and Communications Equipment Cabinet, Enclosure, and Rack Systems” (NWIN) or “Power Distribution Centers for Communication Equipment” (QPQY);

Control equipment intended for use in access control systems providing security protection function, see L69, including:

- Physical access control systems, which provide an attended or unattended means of monitoring or controlling traffic through portals of a protected area for security purposes, or

- Key management systems, which regulate or control access to the use of a device by electrical, electronic or mechanical means.

Access control involves three steps: (a) person(s) requesting access, (b) confirming the credentials of the authorized person(s), and (c) granting access based upon valid credentials / denying access for invalid credentials.

Such equipment is evaluated to the requirements in UL924, are covered under the category for Access Control System Units (ALVY), and intended for installation in accordance with NFPA730 Guide for Premises Security and NFPA731 Standard for the Installation of Electronic Premises Security Systems.

- Electrically operated or mechanically operated control equipment or enclosures intended for theft deterrent or warning purposes, such as detectors or alarms for merchandise or property, property vaults, and safes. Such equipment is evaluated to UL1037, and covered under the category “Antitheft Alarms and Devices” (ATJT).

- Automatic or bypass transfer switches for use in emergency systems, legally required standby systems, or optional standby systems, such equipment is intended to transfer power supplied to loads from one source to another, for example, from utility service to generator service. Such equipment is evaluated to the requirements of UL1008, covered under the categories “Automatic Transfer Switch” (WPWR, WPXT), “Bypass Transfer Switch” (WPVQ) and “Nonautomatic Transfer Switch” (WPYV).

- Equipment primarily intended to energize or de-energize electrical loads to achieve the desired use of electrical power is covered by the Standard for Energy Management Equipment, UL 916. Such equipment is intended to control electrical loads by responding to sensors or transducers monitoring power consumption, by sequencing, by cycling the loads through the use of preprogrammed data logic circuits, or any combination thereof.

# GENERAL

C. As a part of UL's follow-up inspection, it is required that a Field Engineer periodically visit the factory and select, for test or examination or both, samples of production made since the last inspection visit of the products covered.

D. The Follow-Up Service Procedure covering the product is loaned to the manufacturer and constitutes the basis on which the product is judged for compliance with the applicable requirements.

E. Any reference to the term "Standard" applies to UL 508A.

# GENERAL RESPONSIBILITIES OF THE MANUFACTURER AND THE FIELD ENGINEER

F1. The Manufacturer’s and UL Field Engineer’s general responsibilities, as part of the Follow-Up Services Procedure, are as noted in the published document titled, “UL Mark Surveillance Requirements”, and is available through UL’s internet site www.ul.com/fus.  Manufacturers that do not have Internet access may obtain the current version of these requirements from their local UL Customer Service Representative or UL Field Engineer.

F2. 	The UL 508A Industrial Control Panel Listing Program provides two options for panel manufacturers.  Depending on the option used, the manufacturer may be required to have a “Manufacturer’s Technical Representative” (MTR) qualified for the manufacturing location.  Refer to Paragraph G for requirements of an MTR.  The two options are described as follows:

OPTION 1 – UL Evaluated Constructions (MTR Not Required):

This option applies when the construction is fully described in the descriptive section of the UL Follow-Up Services Procedure.  Each labeled industrial control panel produced under this option is also required to comply with applicable parts of the FUII. In addition, the Manufacturer shall monitor construction and component usage to ensure the panels continue to be built in accordance with the descriptive report. Construction modifications that deviate from the descriptive report and are not anticipated by the FUII shall be submitted to UL for evaluation and procedure revision prior to these constructions being labeled with the UL Mark.

OPTION 2 – Enhanced General Coverage (MTR Required):

This option applies when the construction of the product relies on construction requirements in the UL Standard and FUII, rather than being specifically described in the Follow-Up Services Procedure. This option requires a complete review at the factory to confirm compliance with UL 508A for each unique design.  This Option requires the manufacturer to designate a representative (known as an “MTR”) that complies with the requirements detailed in Paragraph G.

G. MANUFACTURER’S TECHNICAL REPRESENTATIVE (MTR)- Each Manufacturer shall designate and maintain at least one representative that meets the criteria of a Manufacturers Technical Representative.  To qualify, this individual shall successfully obtain at least 80% on the UL 508A MTR Qualification EXAM located on the MyAbsorb website https://www.ul.com/LMS. The “MTR” will demonstrate knowledge of UL requirements and be actively involved in the manufacturer’s assessment process to verify compliance with UL requirements. Continued compliance to this requirement will be verified by the UL Field Engineer. Failure to maintain an “MTR” will render the manufacturer ineligible to label Industrial Control Panels and may result in UL Variation Notice and Corrective Action Requirements: UL/C-UL/ULC Mark Follow-Up Services with UL requirements which can be found under Additional Resources at www.ul.com/fus.

# GENERAL INSPECTION GUIDELINES

# APPLICATION OF THE LISTING MARK TO THE PRODUCT

L1 Sample Products: The Field Engineer shall examine at least one sample of the products to verify that the application of the label to the product is in compliance with UL’s requirements.

L2 Certification Mark Requirements: The composition of the UL Mark is described in the Follow-Up Service Procedure.  Additional information, such as camera ready artwork and proportional dimensions for the Marks/Markings, may be found by visiting UL’s website at “http://www.ul.com/marks/ul-listing-and-classification-marks/downloadable-ul-marks/”.  When the Enhanced UL Mark is used, the UL File number shall be provided near the Certification Mark.

L3 Listee Name: The Listee's name, trade name or trademark that identifies the Listee, must appear on the nameplate. The UL File Number that identifies the Listee may appear on the nameplate in lieu of the Listee's name, trade name or trademark.

L4 Mark Applied: Any industrial control panel that is complete with respect to electrical components, electrical enclosure, applicable markings and is in compliance with the applicable requirements shall have a single Listing Mark applied. An industrial control panel that is intended to have components installed in the field shall comply with the guidelines in L63.

L5 Listing Marks: Listing marks for industrial control panels are issued in the following standard labels from UL Label Centers. Listing marks consist of the UL in a circle, the word Listed, a product identification as indicated below and a control or serial number:

- Enclosed Industrial Control Panel – These are standard Listing labels for an industrial control panel provided with an enclosure at the factory.

- Open Industrial Control Panel – These are standard Listing labels for an industrial control panel that includes internal wiring, field wiring terminals, and components mounted on a subpanel without a complete enclosure. The enclosure is intended to be supplied/completed at the installation.

- Industrial Control Panel Enclosure – These are standard Listing labels for the cabinet, either metal or polymeric, used to espouse an industrial control panel. This serves to prevent incidental contact of persons to the industrial control panel and provide a degree of protection for the espoused equipment.

# FIELD ENGINEER’S COUNTERCHECK PROGRAM

L6 Inspection Instructions: The Field Engineer shall examine labeled production for compliance to the requirements in UL 508A, the Follow-Up Service Procedure description (Procedure), and these Follow-Up and Inspection Instructions. The field engineer shall ensure the latest edition of the above documents are available at the manufacturer’s site.

L7 Manufacturers’ Test Program: The Field Engineer shall witness the tests as specified under “Manufacturer’s Test Program” (Table L3).

# INDUSTRIAL CONTROL PANEL ENCLOSURES

L8 Panel Enclosure: The Field Engineer shall confirm an industrial control panel enclosure has been built in compliance with one of the following:

- Type 1 Industrial Control Panel Enclosure – The construction and markings of a metal enclosure are evaluated for compliance with the requirements in Sections 62 – 64 except as noted in 62.2 or as described in the Procedure.

- Type 2-13 Industrial Control Panel Enclosure – A metal enclosure rated as Type 2, 3, 3R, 3RX, 3S, 3SX, 3X, 4, 4X, 5, 6, 6P, 12, 12K, or 13 is evaluated for compliance with the construction and marking requirements described in the Procedure.

- Polymeric (plastic) Industrial Control Panel Enclosure - The construction of a polymeric (plastic) industrial control panel enclosure of any Type rating as indicated in 62.3 are described only in the Procedure .

L9 Enclosure Openings: With the exception of openings allowed in 53.8, 63.4, and 63.5, no openings for components are provided in industrial control panel enclosures unless the dimensions and location of each opening on the enclosure are according to a specific customer drawing. Any such custom-made unfilled openings for components that are provided by the enclosure manufacture do not affect the marked enclosure type rating. Any components installed by the enclosure manufacturer other than those allowed must be described in the Procedure.

L10 Markings: Each industrial control panel enclosure shall be marked as in 64.1 or with the enclosure type rating(s) designating the environmental conditions for which it has been evaluated, such as Type 12 enclosure. A marking that excludes the word Type, such as NEMA 12, is not acceptable.

# COMPONENTS

L11 Category Control Number: A Category Control Number (CCN) is a four or five digit alphanumeric code that identifies product categories in UL Product iQ. UL has categories for each type of component or device. The requirements that the component is evaluated to are based on which category the device is located. These four letters identify the category. The number, or lack of a number, indicates whether the component is Listed or Recognized, as well as whether it is certified to US or Canadian requirements.

XXXX:  No suffix in the CCN indicates that the product is Listed for US

XXXX2: The Suffix “2”  indicates that the product is Recognized for US

XXXX7: The Suffix “7” indicates that the product is Listed for Canada

XXXX8: The Suffix “8” indicates that the product is Recognized for Canada

The Standard contains requirements for specific components to comply with the applicable component standard. There is a document located on UL's Industrial Control Panel website titled UL 508A Supplement SA Specific Component Requirements This document is used to determine the requirements for components used in industrial control panels. This document replaces what was Supplement SA in the Second Edition of UL 508A, and subsequently Appendix C in the Third Edition of UL 508A. The document may be found at; https://www.ul.com/resources/ul-508a-supplement-sa-specific-component-requirements.

Table 1 of Supplement SA contains a reference to each of these requirements by standard number along with the category control number(s) where a list of component manufacturers and additional component information can be found in UL Product iQ. The paragraph in the standard where the component is mentioned is also provided.  A component that is Certified, Listed or Recognized under the category control number cited in Table 1 is considered to comply with the corresponding requirement in the Standard. The component shall also comply with any additional criteria specified in the paragraph referenced in the first column and/or in the ‘Notes’ column of Table 1.

L12 Procedure Description: Where the ‘Notes’ column of SA Table 1 indicates “Procedure described only” or similar, the construction must be submitted for evaluation by UL. Constructions that have been evaluated and found to comply with these requirements are described in the Procedure.  The specific requirements in the Standard that relate to constructions that must be Procedure described are not for use in general coverage.

L13 Industrial Use: Where the “Notes” column of  Table 1 specifies  components that are “Recognized for industrial use”, the specific manufacturer’s Recognition information page in UL Product iQ Directory shall be reviewed to determine whether the component has been certified only for a non-industrial use, in such cases the model number or series is preceded by a product description such as “across-the-line contactors for use in appliances” or “relays for use in information technology equipment”, and any such devices shall not be used unless described in the Procedure. In cases where the model number or series is preceded by a product description that does not declare the intended use, such as “across-the-line contactors”, or is identified for industrial use in addition to one or more other non-industrial uses, such as “across-the-line contactors for industrial use and for use in information technology equipment”, these components are considered suitable for industrial use and procedure description is not required.

L14 Listed Components: Listed Components are identified by the presence of the UL Listing Mark on the product. Listed components shall comply with the requirements in Section 1 of UL 508A Supplement SA Specific Component Requirements

L15 Recognized Components: Recognized components are identified by the UL Recognized component marking as noted in the UL Product iQ Directory. Recognized components shall comply with the requirements in Section 2 of UL 508A Supplement SA Specific Component Requirements.

L16 New/Rebuilt: All components provided in industrial control panels are in a new condition, not having been in service, or marked "Listed Rebuilt" or "Listed Reconditioned".

L17 Other NRTL Components: FOR PANELS BEARING THE UL, cUL or cULus MARK: All components certified by another OSHA Nationally Recognized Testing Laboratory (NRTL) shall either comply with Section 3 of the UL 508A Supplement SA Specific Component Requirements”, or be Procedure described as in L12.

L17a As an alternative to L17, UL, cUL, or cULus industrial control panels may utilize components that are certified by CSA for the US (only) when the CSA certification class of the component is included in Table L1.

1.	Access CSA Certifications Website at ”https://www.csagroup.org/testing-certification/product-listing/”.

2.	Click on the “Product Listing” tab, then search for component (by manufacturer  and keyword) to determine Certification Class (CSA category) and other information pertinent to the component.

3.	Find the CSA Certification Class Number in the first column of Table L1.

a.	Where several UL categories correspond to a single CSA Certification Class, review all of the corresponding UL CCN information in column 3 and instructions for use in column 4.

b.	Review the information on the CSA Component Certification Record, including applicable headings, notes and footnotes and compare to the information in Columns 3 and 4.

c.	Verify the product information does not identify compliance with a UL Standard other than those noted in Table L1;

d.	Verify the CSA Component is the same product type as one of the corresponding UL CCN’s in Column 3 and meets the selection criteria in the associated Column 4 of Table L1;

e.	When the instructions in column 4 indicate the component can be accepted, CSA component usage shall comply with the corresponding requirements in UL508A as noted in Table L1.

f.	When the instructions in column 4 indicate the component must be procedure described, the component can only be used when it is included in this Procedure. For such components that are not described in this Procedure, the manufacturer may submit the complete CSA Certification Report covering the component see L12.

g.	The following information shall be recorded by the manufacturer for CSA components used in Listed Industrial Control Panels according to item 3 above as follows:

| Component Designation | CSA File Number | CSA Class No. | Component Manufacturer’s Name | Catalog Designation | Number Used | Panel Identification |
| --- | --- | --- | --- | --- | --- | --- |

4.	If the CSA Certification Class does not appear in Table L1 or if the component cannot be accepted per Column 4 of Table L1, the component shall comply with the requirements in L17.

Table L1

Component Usage Instructions for CSA Components for US requirements

| CSA CERT. CLASS | CSA CLASS NAME/ STANDARD(S) ON CSA CLASS DESCRIPTION PAGE | UL CCN - CATEGORY NAME/ STANDARD | INSTRUCTIONS FOR USE IN INDUSTRIAL CONTROL PANELS |
| --- | --- | --- | --- |
| 1422-81 | Fuses – Special Type / UL248-1, UL248-14, UL275 | JDYX (JDYX2)– (Component) Fuses, Miscellaneous, Miniature, and Micro / UL248-1, UL248-14 | Fuses covered under this Certification Class cannot be accepted. |
|  |  | JDVS - Fuse Accessories / UL248-1 UL512 | To be accepted, product must be identified as an accessory part without notation to evaluate in the end product, and then assessed to Section 1 of Supplement SA. |
|  |  | JDVS2- Component - Fuse Accessories / UL248-1 UL512 | Products identified as an “accessory” part and with note to evaluate in the end product must be procedure described, see FUII L12, and 2.2 of Supplement SA. |
| 2252-81 2252-81 (Cont.) | Process Control Equipment / UL508 – Part XVII, UL916 Process Control Equipment / UL508 – Part XVII, UL916 | PAZX – Energy Management Equipment / UL916 | Products identified on Certification Record as Energy Management Equipment, or as compliant with UL916, covered under this Certification Class cannot be accepted. |
|  |  | NRAQ - Programmable Controllers / UL508 | Products identified on Certification record as compliant with UL508 without notation to evaluate in the end product, are accepted as compliant with 45.1.1 and additionally assessed to Section 1 of Supplement SA. |
| 2252-91 | Process Control Equipment- Components – Component Acceptance / UL1092, UL508 (Part XVII), Special Bulletin # 94-058 | PAZX2 –Component - Energy Management Equipment / UL916 | Products identified on Certification Record as Energy Management Equipment, or as compliant with UL916, covered under this Certification Class cannot be accepted. |
|  |  | NRAQ2 – Component - Programmable Controllers / UL508 | Products identified on Certification record as compliant with UL508 without notation to evaluate in the end product, are accepted as compliant with 45.1.1 and additionally assessed to Section 2 of Supplement SA. |
| 3211-83 | Auxiliary Devices / UL50, UL508 | NRGU – Protective Relays / UL508 | Products identified on Certification Record as protective relay without note to evaluate in the end product are not acceptable for use in industrial control panels. |
|  |  | NRGU2 – Component – Protective Relays / UL508 | Products identified on Certification Record as protective relay with note to evaluate in the end product are not acceptable for use in industrial control panels. |
|  |  | SWIV2 – Component - Relay Sockets and Assemblies / UL508 | Products identified on Certification record as a relay socket compliant with UL508 with notation to evaluate in the end product, are accepted as compliant with 45.1.1 and additionally assessed to Section 2 of Supplement SA. |
| 3211-84 | Magnetic Motor Controllers / UL50, UL347, UL508, UL845 | NJHU – Motor Controllers over 1500V / UL347 | Motor controllers identified on Certification Record as compliant with UL347, or rated over 1500V, covered under this Certification Class cannot be accepted. |
|  |  | NJAV – Motor Control Centers / UL845 | Motor Control Center Sections and Units covered under this Certification Class cannot be accepted. |
|  |  | NLDX -Magnetic Motor Controllers/ UL508 | Products identified on Certification record as a contactor or starter compliant with UL508 without notation to evaluate in the end product, are accepted as compliant with 33.1.1 and additionally assessed to Section 1 of Supplement SA. |
| 3211-85 | Manual Motor Controllers / UL50, UL508 | NLRV - Manual Motor Controllers / UL508 | Products identified on Certification record as compliant with UL508 without notation to evaluate in the end product, are accepted as compliant with 33.1.1 and additionally assessed to Section 1 of Supplement SA. |
|  |  | NLRV2 – Component - Manual Motor Controllers / UL508 | 1. Products identified on Certification record as compliant with UL508 for industrial use with notation to evaluate in the end product, are accepted as compliant with 33.1.1 and additionally assessed to Section 2 of Supplement SA. 2. Products identified on Certification record for non-industrial use must be procedure described, see FUII L12, and 2.2 of Supplement SA. |
| 3211-86 | Miscellaneous Motor Controllers / UL347, UL347A, UL508, UL508C | NITW – Industrial Control Panels / UL508A | Products identified on Certification Record as special industrial control assemblies, without notation to evaluate in the end product, covered under this Certification Class cannot be accepted. |
|  |  | NJHU – Motor Controllers over 1500V / UL347 | Motor controllers identified on Certification Record as compliant with UL347, or rated over 1500V, covered under this Certification Class cannot be accepted. |
|  |  | NJIC – Power Conversion Equipment, Medium Voltage / SU347A | Products identified on Certification Record as compliant with UL347A or rated over 1500V covered under this Certification Class cannot be accepted. |
|  |  | NKPZ - Float and Pressure operated motor controllers / UL508 | Products identified on Certification record as a float or pressure operated motor controller compliant with UL508 without notation to evaluate in the end product, are accepted as compliant with 33.1.1 and additionally assessed to Section 1 of Supplement SA. |
|  |  | NMFT - Miscellaneous Motor Controllers / UL508 | Products identified on Certification record as compliant with UL508 without notation to evaluate in the end product, are accepted as compliant with 33.1.1 and additionally assessed to Section 1 of Supplement SA. |

| 3211-86 (Cont.) | Miscellaneous Motor Controllers / UL347, UL347A, UL508, UL508C | NMFT2 – Component - Miscellaneous Motor Controllers / UL508 | Solid-state motor controllers identified on Certification record as compliant with UL508 with notation to evaluate in the end product must be procedure described, see FUII L12, and 2.1 and Table 1 of Supplement SA. |
| --- | --- | --- | --- |
|  |  | NMMS - Power Conversion Equipment / UL508C | Products identified on Certification record as compliant with UL508C without notation to evaluate in the end product, are accepted as compliant with 33.1.2 and additionally assessed to Section 1 of Supplement SA. |
|  |  | NMMS2 - Power Conversion Equipment / UL508C | Product identified on Certification record as compliant with UL508C with notation to evaluate in the end product must be procedure described, see FUII L12, and 2.1 and Table 1 of Supplement SA. |
| 3211-87 | Miscellaneous Apparatus / UL50, UL508, UL347 | NJHU – Motor Controllers over 1500V / UL347 | Products identified on Certification Record as compliant with UL347, or rated over 1500V, covered under this Certification Class cannot be accepted. |
|  |  | NITW – Industrial Control Panels / UL508A | 1. Products identified on Certification Record as special industrial control assemblies, covered under this Certification Class cannot be accepted. 2. Products identified as an enclosure or special purpose enclosure without notation to evaluate in the end product, are accepted as compliant with 18.3 and additionally assessed to Section 1 of Supplement SA. |

| 3211-87 (cont) | Miscellaneous Apparatus / UL50, UL508, UL347 | NITW2 – Component - Industrial Control Panels / UL508A | Products identified on Certification record as an enclosure, a ventilation kit, observation window kit, fan kit, cabinet heater kit, or a cabinet lighting package, compliant with UL508 for industrial use with notation to evaluate in the end product, are accepted as compliant with 18.3(b), 21.1.1, 23.1, 26.2.3, 26.4.2, and 27.2.3, respectively, and additionally assessed to Section 2 of Supplement SA. |
| --- | --- | --- | --- |
|  |  | NKCR - Auxiliary Devices / UL508 | Products identified on Certification record as a switch or pilot light, compliant with UL508 without notation to evaluate in the end product, are accepted as compliant with 45.1.1 or 46.1.1 and additionally assessed to Section 1 of Supplement SA. |
|  |  | NKCR2 – Component - Auxiliary Devices / UL508 | 1. Products identified on Certification record as a pushbutton switch or pilot light compliant with UL508 for industrial use with notation to evaluate in the end product, are accepted as compliant with 45.1.1 or 46.1.1 and additionally assessed to Section 2 of Supplement SA. 2. Products for non-industrial use with notation to evaluate in the end product must be procedure described, see FUII L12, and 2.1 and Table 1 of Supplement SA. |
|  |  | NKPZ2 - Float and Pressure operated motor controllers / UL508 | 1. Products identified on Certification record as a float or pressure operated motor controller compliant with UL508 for industrial use with notation to evaluate in the end product, are accepted as compliant with 33.1.1 and additionally assessed to Section 2 of Supplement SA. 2. Products for non-industrial use with notation to evaluate in the end product must be procedure described, see FUII L12, and 2.1 and Table 1 of Supplement SA. |
| 3211-87 (cont) | Miscellaneous Apparatus / UL50, UL508, UL347 | NMTR - Miscellaneous Apparatus / UL508 | To be accepted, product must be identified on Certification record as compliant with UL508 without notation to evaluate in the end product, and then assessed to Section 1 of Supplement SA. |
|  |  | NMTR2 – Component - Miscellaneous Apparatus / UL508 | To be accepted, product must be identified on Certification record as compliant with UL508 with notation to evaluate in the end product, and then assessed to Section 2 of Supplement SA. |
|  |  | SWIV2 – Component - Relay Sockets and Assemblies / UL508 | Products identified on Certification record as a relay socket compliant with UL508 without notation to evaluate in the end product, are accepted as compliant with 45.1.1 and additionally assessed to Section 2 of Supplement SA. |
| 3211-91 | Enclosures for Electrical Equipment / UL50, UL50E | CYIV – Cabinets and Cutout Boxes/ UL50, UL50E | Products are additionally assessed to Section 1 of Supplement SA. |
| 3215-90 | Supplementary Protectors - Component Acceptance / UL1077 | QVNU2 – Component - Supplementary Protectors / UL1077 | Product must be assessed to the requirements for supplementary protectors specified in Supplement SA. |
| 3231-81 | Switches- Automatic- Magnetic Type / UL508 | NLDX2 – Component - Magnetic Motor Controllers / UL508 | 1. Products with motor rating for industrial use are accepted as compliant with 45.1.1 and additionally assessed to Section 2 of Supplement SA. 2. Products for non-industrial use with notation to evaluate in the end product must be procedure described, see FUII L12, and 2.1 and Table 1 of Supplement SA. |
|  |  | NRNT2 – Component - Industrial Control Switches | 1. Products without motor rating for industrial use are accepted as compliant with 45.1.1 and additionally assessed to Section 2 of Supplement SA. 2. Products for non-industrial use with notation to evaluate in the end product must be procedure described, see FUII L12, and 2.1 and Table 1 of Supplement SA. |
| 3231-82 | Switches- Automatic- Pressure Type / UL508 | NKPZ - Float and Pressure operated motor controllers | Products identified on Certification record as a pressure operated motor controller compliant with UL508 without notation to evaluate in the end product, are accepted as compliant with 33.1.1 and additionally assessed to Section 1 of Supplement SA. |
|  |  | NKPZ2 – Component - Float and Pressure operated motor controllers | 1. Products must be identified on Certification record as a pressure operated motor controller compliant with UL508 with notation to evaluate in the end product, are accepted as compliant with 33.1.1 and additionally assessed to Section 2 of Supplement SA. 2. Products identified on Certification record as for non-industrial use with notation to evaluate in the end product must be procedure described, see FUII L12, and 2.1 and Table 1 of Supplement SA. |
| 3231-94 | Switches- Component– Automatic-Industrial Control / UL508 | NRNT2 – Component - Industrial Control Switches | 1. Products for industrial use are accepted as compliant with 45.1.1 and additionally assessed to Section 2 of Supplement SA. 2. Products for non-industrial use with notation to evaluate in the end product must be procedure described, see FUII L12, and 2.1 and Table 1 of Supplement SA. |
| 4621-82 | Panelboard and Switchboard Accessories / UL67 | QEUY2 – Component - Panelboard and Switchboard Accessories / UL67 | Unable to evaluate these components at this time |
| 4632-81 | Service Equipment – Service and Metering Equipment / UL67, UL98, UL414, UL508, UL869, UL869A | PJWT – Meter Socket Bases/ UL414 | To be accepted, product must be identified as a meter socket base without notation to evaluate in the end product, and then assessed to Section 1 of Supplement SA. |
| 4632-81 (Cont.) | Service Equipment – Service and Metering Equipment / UL67, UL98, UL414, UL508, UL869, UL869A | PKAX – Meter Socket Accessories / UL414 | To be accepted, product must be identified as an accessory part without notation to evaluate in the end product, and then assessed to Section 1 of Supplement SA. |
|  |  | PKAX2 – Component – Meter Socket Accessories / UL414 | Products identified on Certification Record as an “accessory” part, such as enclosures, jaws, and blades, and with note to evaluate in the end product must be procedure described, see FUII L12, and 2.2 of Supplement SA. |
|  |  | POCQ2 – Component – Meter Socket Bases and Associated Assemblies / UL414 | Products identified on Certification Record as a meter socket base with note to evaluate in the end product or any other assemblies must be procedure described, see FUII L12, and 2.2 of Supplement SA. |
|  |  | QEUY – Panelboards / UL67 | Products identified on Certification Record as a panelboard, or compliant with UL67, covered under this Certification Class cannot be accepted. |
| 4652-84 | Switches- Miscellaneous / UL20, UL67, UL98, UL508, UL773, UL773A, UL891 | WJQR – Snap Switches / UL20 | Products identified on Certification Record as a general use snap switch, such as a door, fixture, flush, pendant or surface switch, or compliant with UL20, covered under this Certification Class cannot be accepted. |
|  |  | WHXS – Switches, Dead-Front / UL98 | Products identified on Certification Record as a dead-front switch, or compliant with UL98, covered under this Certification Class cannot be accepted. |
|  |  | WIAX – Switches, Enclosed / UL98 | Products identified on Certification Record as an enclosed switch, or compliant with UL98, covered under this Certification Class cannot be accepted. |
|  |  | WJFX - Photo Controls, Plug-In, Locking Type / UL773 | WJFX - Photo Controls, Plug-In, Locking Type / UL773 |
| 4652-84 (Cont.) | Switches- Miscellaneous / UL20, UL67, UL98, UL508, UL773, UL773A, UL891 | WJCT – Switches, Photoelectric / UL773A | Products identified on Certification Record as a non-industrial photoelectric switch, or compliant with UL773A, covered under this Certification Class cannot be accepted. |
|  |  | WEVZ – Dead-front Switchboards / UL891 | Products identified on Certification Record as a dead-front switchboard, or compliant with UL891, covered under this Certification Class cannot be accepted. |
|  |  | NRNT - Industrial Control Switches / UL508 | Products identified on Certification record as compliant with UL508 without notation to evaluate in the end product, are accepted as compliant with 45.1.1 and Section 1 of Supplement SA. |
|  |  | NRNT2 – Component - Industrial Control Switches / UL508 | Products identified on Certification record as compliant with UL508 and with notation to evaluate in the end product, are accepted as compliant with 45.1.1 and additionally assessed to Section 2 of Supplement SA. |
| 4652-86 | Switches- Moulded Case / UL489 | WJAZ – Switches, Molded Case / UL489 | Products are accepted as compliant with 30.1.2 of UL508A for use as a disconnecting means |
| 4812-82 | Ground Fault Devices – Signal Type Detectors / UL1053 | KDAX - Ground-Fault Sensing and Relaying Equipment / UL1053 | 1. Products identified as a “ground fault sensing and relaying controller” part and without notation to evaluate in the end product are accepted as compliant with 75.6.1 of UL508A. 2. Products identified as a “monitor” without notation to evaluate in the end product do not comply with 75.6.1 but can be assessed to Section 1 of Supplement SA. |

| 4812-82 (cont) | Ground Fault Devices – Signal Type Detectors / UL1053 | KDAX2 – Component - Ground-Fault Sensing and Relaying Equipment / UL1053 | 1. Products identified as a “ground fault sensing and relaying controller” part and with note to evaluate in the end product must be procedure described, see FUII L12, 75.6.1 and 2.2 of Supplement SA. 2. Products identified as a “monitor” and with note to evaluate in the end product do not comply with 75.6.1 and must be procedure described, see FUII L12, and 2.2 of Supplement SA. |
| --- | --- | --- | --- |
| 6225-81 | Fuseholder Assemblies / UL512 | IZLT - Fuseholders, Cartridge Fuse / UL512 | 1. Products identified for use with Class rated fuses, other than Class C, CA, and CB, and without notation for evaluation in end use, are accepted as compliant with 31.1.5 and assessed to Section 1 of Supplement SA. 2. Products identified for use with supplementary fuses and without notation for evaluation in end use, are accepted as compliant with 40.1.4 and assessed to Section 1 of Supplement SA. 3. Products identified for use with Class C, CA, and CB fuses covered under this Certification Class cannot be accepted. |
|  |  | IZLT2 – Component - Fuseholders, Cartridge Fuse / UL512 | 1. Products identified for use with Class rated fuses, other than Class C, CA and CB, and with notation for evaluation in end use, are accepted as compliant with 31.1.5 and assessed to Section 2 of Supplement SA. 2. Products identified for use with supplementary fuses and with notation for evaluation in end use, are accepted as compliant with 40.1.4 and assessed to Section 2 of Supplement SA. 3. Products identified for use with Class C, CA, and CB fuses covered under this Certification Class cannot be accepted. |
| 6225-81 (cont) | Fuseholder Assemblies / UL512 | JAMZ – Plug Fuse, Fuseholders / UL248-1, UL512 | Products identified for use with plug fuses and without notation for evaluation in end use, are accepted as compliant with 31.1.5 and assessed to Section 1 of Supplement SA. |
|  |  | JAMZ2 – Component – Plug Fuse, Fuseholders / UL248-1, UL512 | Products identified for use with plug fuses and with notation for evaluation in end use, are accepted as compliant with 31.1.5 and assessed to Section 2 of Supplement SA. |
|  |  | JDVS - Fuse Accessories / UL248-1, UL512 | To be accepted, product must be identified as an accessory part without notation to evaluate in the end product, and then assessed to Section 1 of Supplement SA. |
|  |  | JDVS2 – Component - Fuse Accessories / UL248-1, UL512 | Products identified as an “accessory” part and with note to evaluate in the end product must be procedure described, see FUII L12, and 2.2 of Supplement SA. |
| 6228-81 | Wire Connecting Devices – Terminal Assemblies / UL1059 | XCFR2 – Component - Terminal Blocks / UL1059 | 1. Products identified with voltage rating, current rating, wire range, terminal tightening torque, and spacing group A, C or D, are accepted as compliant with 28.2.1 for field wiring use when ratings and spacings are suitable for the application. 2. Products where voltage rating, current rating, wire range, terminal tightening torque, and/or spacing group A, C or D, information is not available must be procedure described, see FUII L12, and 2.2 of Supplement SA. |
| 6231-81 | Lampholders- Electric Discharge- More than 1000V / UL542, UL879 | OOIX - Lampholders, Miscellaneous / UL496 | Lampholders identified on Certification Record as compliant with UL542 or UL879, or rated over 1000V, covered under this Certification Class are not acceptable for use in industrial control panels. |
|  |  | OOIX2 – Component – Lampholders, Miscellaneous / UL496 | Lampholders identified on Certification Record as compliant with UL542 or UL879, or rated over 1000V, covered under this Certification Class are not acceptable for use in industrial control panels. |

| 6231-87 | Lampholders- Incandescent- Medium Base / UL496, UL1054 | ONHR – Lampholders, Medium Base / UL496 | Products identified on Certification Record as a Medium base lampholder covered under this Certification Class cannot be accepted. |
| --- | --- | --- | --- |
|  |  | OOIX - Lampholders, Miscellaneous / UL496 | To be accepted, products identified as a pilot light without notation for evaluation in end use, are accepted as compliant with 46.1.1 and assessed to Section 1 of Supplement SA. |
| 6231-89 | Lampholders- Incandescent- Mogul Base / UL496, UL1054 | ONUZ – Lampholders, Mogul Base / UL496 | Products identified on Certification Record as a Mogul base lampholder covered under this Certification Class cannot be accepted. |
|  |  | OOIX2 – Component - Lampholders, Miscellaneous / UL496 | Products as a pilot light with notation for evaluation in end use, are accepted as compliant with 46.1.1 and assessed to Section 2 of Supplement SA. |

L18 Canadian Certification: FOR PANELS BEARING THE cUL or cULus MARK: Components are additionally required to comply with Canadian Standards. This can be verified through cUR or cUL certification. Components certified by other certification bodies shall comply with the requirements in L17.  All warning and Caution labels on a Listed cUL or cULus 508A panel that may be shipped to Canada shall be marked as specified in Canadian Certification Requirements for Bilingual Safety, Warning and Caution Markings which can be found in the Additional Resources at www.ul.com/fus.

L18a As an alternative to L18, c-UL (or c-UL-us) industrial control panels may utilize components that are (1) Certified by UL for the US, and also (2) certified by CSA for Canada when the CSA certification class of the component is included in Table L2.

1.	Access CSA Certifications Website at ”https://www.csagroup.org/testing-certification/product-listing/”.

2.	Click on the “Product Listing” tab, then search for component (by manufacturer  and keyword) to determine Certification Class (CSA category) and other information pertinent to the component.

3.	Find the CSA Certification Class Number in the first column of Table L2.

a.	Where several UL categories correspond to a single CSA Certification Class, review all of the corresponding UL CCN information in column 3 and instructions for use in column 4.

b.	Review the information on the CSA Component Certification Record, including applicable headings, notes and footnotes and compare to the information in Columns 3 and 4.

c.	Verify the product information does not identify compliance with a CSA Standard or a UL Standard other than those noted in Table L2;

d.	Verify the CSA Component is the same product type as one of the corresponding UL CCN’s in Column 3 and meets the selection criteria in the associated Column 4 of Table L2;

e.	When the instructions in column 4 indicate the component can be accepted, CSA component usage shall comply with the corresponding requirements in UL508A as noted in Table L2.

f.	When the instructions in column 4 indicate the component must be procedure described, the component can only be used when it is included in this Procedure. For such components that are not described in this Procedure, the manufacturer may submit the complete CSA Certification Report covering the component see L12.

g.	The following information shall be recorded by the manufacturer for CSA components used in Listed Industrial Control Panels according to item 3 above as follows:

| Component Designation | CSA File Number | CSA Class No. | Component Manufacturer’s Name | Catalog Designation | Number Used | Panel Identification |
| --- | --- | --- | --- | --- | --- | --- |

4.	If the CSA Certification Class does not appear in Table L2  or if the component cannot be accepted per Column 4 of Table L2, the component shall comply with the requirements in L17.

Table L2

Component Usage Instructions for CSA Components for Canadian requirements

| CSA CERTIFICATION CLASS | CSA CLASS NAME | UL CCN/CATEGORY NAME | INSTRUCTIONS FOR USE IN INDUSTRIAL CONTROL PANELS |
| --- | --- | --- | --- |
| 3211-03 | Auxiliary Devices | NKCR7 – Auxiliary Devices |  |
| 4412-01, -02, -03 | Conduit Fittings | ILNR7/Fittings, Flexible Metallic Tubing; QCRV7/ Outlet Bushings and Fitting |  |
| 5853-01 | Appliance Wiring Material | AVLV8 - Component - Appliance Wiring Material |  |
| 4413-02 | Cover Plates for Flush-Mounted Wiring Devices | QCIT7/Metallic Outlet Boxes |  |
| 6241-01 | Dimmer Switches | EOYX7/ Dimmers, General-use Switch |  |
| 2221-51 | Fixed Capacitors for Use in Electronic Equipment | FOWX8 – Component – Fixed Capacitors for Use in Electronic Equipment |  |
| 1422-01, -30 | Supplemental Fuses | JDYX8 – Component - Fuses, Supplemental |  |
| 6225-01 | Fuse Accessories | JDVS7/Fuse Accessories |  |
| 6225-01 | Fuseholders, Cartridge Fuse | IZLT7/Fuseholder, Cartridge Fuse |  |
| 4415-01, -02; 4412-02 | Hardware for the Support of Conduit, Tubing, and Cable | DWMU7/Conduit and Cable Hardware |  |
| 9052-01 | Insulating Bushings | NZMT8 – Component - Insulating Bushings |  |
| 5841-01, -02, -03; 5842-01, -02, -03 | Power supply cord & Detachable cord set | ELBZ7/Cord Sets and Power-supply Cords |  |
| 3426-32 | LED driver | FKSZ7/Light-emitting-diode Drivers |  |
| 1813-01 | Liquid-Tight Flexible Nonmetallic Conduit | DXOQ7/Flexible Nonmetallic Conduit, Liquid-tight |  |
| 4411-01; 4412-02 | Metallic Outlet Boxes | QCIT7/Metallic Outlet Boxes |  |
| 1852-01; 4511-01 | Nonmetallic Conduit & Associated Fittings | FKHU7/Electrical Nonmetallic Tubing; FKKY7/Electrical Nonmetallic Tubing Fittings |  |
| 1853-01; 4511-02 | Nonmetallic Mechanical Protection Tubing (NMPT) | YDRQ8 – Component - Tubing, Mechanical Protection and Fittings |  |
| 4681-04, -05 | Nonmetallic Surface Raceways and Fittings | RJYT7/Surface Nonmetallic Raceway Fittings |  |
| 6225-01, -02 | Plug Fuse, Fuseholders | JAMZ7/Fuseholder, Plug Fuse |  |
| 6233-01 | Plugs, Receptacles, and Cable Connectors of the Pin and Sleeve Type | QLGD7/Pin-and-Sleeve-type Plugs, Receptacles and Cable Connectors |  |
| 4414-09 | Positioning Devices | ZODZ7/Positioning Devices |  |
| 3211-03, -07 | Protective Relays | NRGU7/Protective Relays |  |
| 3215-30 | Protectors, Supplementary – Component | QVNU8 – Component - Protectors, Supplementary | Products are additionally assessed to Supplement SA. |
| 6227-01 | Quick Connects | RFWV7/Electrical Quick-connect Terminals |  |
| 3211-07, -03 | Relay Sockets and Assemblies – Component | SWIV8 – Component - Relay Sockets and Assemblies | Products identified on Certification record as a relay socket without notation to evaluate in the end product, are accepted as compliant and additionally assessed to Section 2 of Supplement SA. |
| 6241-05, -08 | Snap Switches | WLFV7/Switches, Door;WMUZ7/Switches, Flush; WNIX7/Switches, Pendant; WOKT7/Switches, Surface |  |
| 6223-02 | Splicing Wire Connectors | ZMVV7/Wire Connectors and Soldering Lugs |  |
| 9091-32, 2213-01, -31 | Surge Protective Devices | VZCA8/Surge-protective Devices |  |
| 4651-01 | Switches, Enclosed | WIAX7/Switches, Enclosed |  |
| 4652-04; 3231-01, -52 | Switches, Industrial Control | NRNT7/Switches, Industrial Control |  |
| 4813-01, -02; 4823-01, -02 | Temperature Indicating & Regulating Equipment | XAPX7/Temperature-indicating and -Regulating Equipment |  |
| 6228-01 | Terminal Blocks | XCFR8/Terminal Blocks | Products are additionally assessed to Section 2 of Supplement SA. |
| 5841-02, -02, -03 | Flexible cord | ZJCZ7/Flexible Cord |  |
| 6323-02 | Wire Connectors | ZMVV7/Wire Connectors and Soldering Lugs |  |
| 2252-01 | Programmable Controllers | NRAQ7/ Programmable Controllers |  |
| 3211-07 | Magnetic Motor Controllers | NLDX7/Motor Controllers, Magnetic |  |
| 3211-05 | Manual Motor Controllers | NLRV7/Motor Controllers, Manual |  |
| 3211-09 | Industrial Control Panels | NITW7/Industrial Control Panels | Products identified as an enclosure or special purpose enclosure without notation to evaluate in the end product, are accepted as compliant and additionally assessed to Section 1 of Supplement SA. |
| 3211-09 | Industrial Control Panels - Component | NITW8 – Component - Industrial Control Panels | Products identified on Certification record as an enclosure, a ventilation kit, observation window kit, fan kit, cabinet heater kit, or a cabinet lighting package with notation to evaluate in the end product, are accepted as compliant and additionally assessed to Section 2 of Supplement SA. |
| 3211-11 | Enclosures for Electrical Equipment | CYIV7/Cabinets and Cutout Boxes |  |
| 3211-06 | Float and Pressure operated motor controllers | NKPZ7/Motor Controllers, Float- and Pressure-operated |  |
| 3211-06 | Miscellaneous Motor Controllers | NMFT7/Motor Controllers, Mechanically Operated and Solid-state |  |
| 3211-16 | Power Conversion Equipment | NMMS7/Power Conversion Equipment |  |
| 3211-36 | Power Conversion Equipment - Component | NMMS8 – Component - Power Conversion Equipment |  |
| 3211-07 | Miscellaneous Apparatus | NMTR7/Power Circuit and Motor-mounted Apparatus |  |
| 4632-01 | Meter Socket Bases | PJWT7/Meter-socket Bases |  |
| 4632-01 | Meter Socket Accessories | PKAX7/Meter-socket Accessories |  |
| 4621-01 | Panelboards | QEUY7/Panelboards |  |
| 6241-10 | Snap Switches | WJQR7/Snap Switches |  |
| 4651-02 | Switches, Dead-Front | WHXS7/Switches, Dead-front |  |
| 4652-04 | Switches, Photoelectric | WJFX7/Photocontrols, Plug-in, Locking Type |  |
| 4652-06 | Switches, Molded-Case | WJAZ7/Switches, Molded Case |  |
| 4812-02 | Ground-Fault Sensing and Relaying Equipment | KDAX7/Ground-fault Sensing and Relaying Equipment |  |
| 6231-09 | Lampholders, Miscellaneous | OOIX7/Lampholder, Miscellaneous |  |

L19 Optional Components:

Circuit Breaker Accessories - The following R/C (DIHS2) Circuit breaker Accessories or R/C (QEUY2) Panelboard Accessories which do not require disassembly of the circuit breaker may be used without further evaluation:

- Mechanical devices (such as handles, operators, operating mechanisms, mounting brackets, standoffs etc.)

- Electrical terminals such as lug kits and neutral/ground bars for internal wiring connections or used as field wiring terminals. They shall be used within their rated wire range and marked with the tightening torque indicated in the kit instructions. Neutral bars shall be electrically isolated from grounded metal by insulators and with electrical spacing maintained per UL508A.

These components are installed in combination with the circuit breakers or other devices as described in their installation instructions.  Devices, which mount through an opening in the enclosure, are suitable for use on Type 1 enclosures only unless otherwise indicated.

# CONSTRUCTION

L20 General: The construction requirements in Sections 7-17 apply to all industrial control panels. A panel that complies with applicable requirements in the Standard complies with section 7. Industrial control panels for other uses, or containing features or components that are not specifically addressed by the Standard must be described in the Procedure.

L21 Spacings: When an industrial control panel utilizes components that have been previously certified by UL, the component is considered in compliance with 10.1 and the Field Engineer is not required to review spacings at and within a component. The Field Engineer is not required to review the spacings at and within a component installed in accordance with Appendix B.

L22 Spacings Between Components: The Field Engineer shall verify spacings between components and between components and uninsulated grounded parts, and between components and the walls of a metal enclosure for compliance with the spacing requirements in Section 10. Where insufficient spacings are found, the use of an insulating barrier, such as a liner on an enclosure wall or an insulating tubing, or a sheet or molded piece of insulating material, such as a standoff, may be installed in order to comply with the requirements in Section 10.  The generic materials noted in Tables 12.1 and 13.1 comply with 12.2 and 13.2 respectively when used at not less than the minimum thickness specified.

L23 Grounding and Bonding: All industrial control panels shall comply with the requirements in Sections 14 – 17.

L24 Power Supply Grounding: The secondary circuits of power supplies are subject to the secondary grounding requirements in Section 16 based on the voltage source to the primary, the secondary voltage ratings and the presence of field wiring terminals in the secondary circuit. When the secondary circuit is required to be grounded, the grounded circuit conductor on the secondary circuit of a power supply shall comply with the color-coding requirements in 17.4.

L25 Slash Voltage Grounding: The secondary circuit of a transformer or power supply shall be grounded as in 16.3 when components, such as overcurrent protection devices, with slash voltage ratings, such as 120/240, 480Y/277, or 600Y/347, are supplied in the secondary circuit. The requirement in 16.3 applies to these constructions whether or not the secondary circuit is required to be grounded per 16.1.

# ENCLOSURE

L26 General Enclosure: Each enclosed industrial control panel shall comply with the requirements in Sections 18-27 and with any additional requirements contained in the Procedure. An enclosed industrial control panel includes the enclosure, the components contained within the enclosure and components mounted to or through the walls of the enclosure. Except as noted in 18.1, for portions of an open industrial control panel that serve to complete an ultimate enclosure after installation, the Part 1 requirements for enclosed industrial control panels, sections 18-27, are not used to evaluate open industrial control panels. An open industrial control panel consists of the mounting panel and all components mounted to it.

L27 Enclosure Type Ratings: Each opening in an enclosure of an enclosed industrial control panel with a rating other than Type 1 shall be filled or  covered by a component having a Type rating as specified in 19.3 or 19.4  where the Type rating shall be established by:

- Markings provided on the component,

- Described in the literature accompanying the component, or

- As described in UL Product iQ.

L28 Component Type Ratings: Hardware type components penetrating the enclosure of an enclosed industrial control panel (such as a screw, bolt, rivet, or similar component) with a rating other than Type 1 shall have a Type rating as specified in 19.3 or 19.4  where the Type rating shall be established by:

- Markings provided on the component,

- Described in the literature accompanying the component, or

- As described in UL Product iQ.

- Unless specified in a), b), or c) above, a sealant is permitted for an enclosure rated Type 1 and shall be described in the Procedure if used to maintain a rating other than Type 1.

L29 Arcing Parts Spacings: Components having a possible source of arcing, as specified in 22.1, including power circuit components that may produce an arc during normal operation, such as a disconnect switch, the vent openings of a circuit breaker, a contactor or an overload relay, shall be located at least 12 inches (305 mm) from a ventilation opening. This does not include components:

- where the arcing is fully contained within the component’s enclosure or casing (such as an enclosed variable speed drive),

- where no arcing is produced during normal operation (such as a solid state relay),

- otherwise protected by a barrier in accordance with Paragraphs 22.2 through 22.5, or

- located within a control circuit.

# POWER CIRCUITS

L30 General: Each industrial control panel provided with one or more components that will be connected in the field into a power circuit shall comply with the requirements in Sections 28-36 based on the electrical ratings established by the manufacturer for each input and output circuit.

L31 Field Wiring: All panels are required to comply with Section 28 for all electrical connections to the input power supply and loads located outside of the panel.

L32 Multiple Conductors: Number of conductors installed in a conduit or raceway – when four or more conductors, other than a neutral that carries an unbalanced current, are installed or intended to be field installed in a conduit or raceway, they shall have an ampacity at a reduced percentage as described in Table 28.1 Note 2. The number of conductors in the count shall  include only those conductors that are connected to electrical components that are able to be simultaneously energized.

L33 Internal Wiring: All panels are required to comply with Section 29 for all factory provided electrical connections between components provided as part of the panel. Printed wiring boards shall not be used for factory connections between components of a power circuit unless Procedure described, or an integral part of a Listed or Recognized component.

L34 Class B and C Conductors: Internal conductors are Class B or C (if no marking is available to determine the class, then use the following guidelines: 19 strands maximum for conductors 14 to 4/0 AWG; 37 strands maximum for conductors 250 KCMIL or larger) and sized in accordance with 29.6.1 using Table 28.1. Conductors shall be selected based on the terminal temperature rating marked on each component, i.e. 60C or 75C. A component marked 60/75C may use a conductor based on either column of Table 28.1. For components that are unmarked and rated 100A, or less or are marked with different terminal temperature ratings, the conductors shall be selected based on 60C. For components that are unmarked and rated more than 100A , the conductors shall be selected based on 75C.

L35 Flexible Conductors: Flexible conductors, including machine tool wire identified as “Flexing” or “Class K” (if no marking is available to determine the class, then use the following guidelines: equal number of strands to Class B and C conductors for 18 AWG and smaller; 26 strands minimum for 16 AWG; 41 strands minimum for 14 AWG; 65 strands minimum for 12 AWG; 104 strands minimum for conductors 10 AWG or larger) and welding cable, shall only be used when terminated into pressure wire connectors, such as terminal blocks, terminals of components, or crimp-on terminals that comply with 29.3.12 and are described in the Procedure as suitable for the size and type of the flexible conductor to be used.

L36 Multiple Conductor Termination: Multiple conductors may be secured to a single termination point. There is no limit to the number of conductors that may be secured to a single terminal, provided that all requirements specified in 29.3.7 are met.

L37 Flexible Bus Bar: Flexible bus bar is treated as wire or a flat conductor (Listed or Recognized AWM). There is no SCCR required. Flexible bus bar shall be routed in accordance with 29.4. Flexible bus bar is covered by Recognitions under QEUY2 and optionally covered under AVLV2.  Recognitions under AVLV2 do not require Procedure description. Recognitions under QEUY2 require Procedure description. The ampacity of busbars Recognized under AVLV2 shall be determined by using Table 28.1 and comparing their cross-sectional area to the equivalent conductor size in the table. Alternatively, their ampacity may be determined based on their current density not exceeding 1000 amperes per square inch (per 6.45 cm2) of cross-sectional area (minimum width of bus bar multiplied by minimum thickness of bus bar) of the copper bus bar. Recognized bus bar systems, including flexible bus bars covered under QEUY2, shall have all construction details described in the Procedure.

L38 Disconnecting Means: A disconnecting means is not required to be part of an industrial control panel and may be provided in an industrial control panel with or without branch circuit protection, see 30.3.1.  A disconnecting means provided as a part of an industrial control panel shall comply with Section 30.

L39 Combination Motor Controllers: In lieu of specific Procedure description noted in Table 1 of “UL 508A Supplement SA Specific Component Requirements”, combination motor controllers can be constructed using the specific manufacturer and part number of a Recognized instantaneous trip circuit breaker, motor controller, overload relay and any other associated components and combination ratings described on the UL website, see L58.

L40 Branch Circuit Protection: Branch circuit protection is not required to be a part of an industrial control panel, and branch circuit type fuses are not required to be installed in rejection type fuseholders provided in a panel, see 31.2.1.  Branch circuit protection or rejection type fuseholders provided as part of an industrial control panel shall comply with the requirements in Section 31 that apply for each of the intended loads, i.e. motor, receptacle, heater, appliance, or lighting, to be supplied from the panel. Starting from the load side of the panel, the branch circuit protection is the first component that complies with 31.1.1 – 31.1.6. Any of the components noted in 31.1.7 shall be ignored with respect to determining compliance with Section 31.

L41 For Future Use:

L42 Branch Circuit Protection of Motor Groups: The branch circuit protection for a motor shall be verified to comply with the requirements for a motor group, 31.4, when the branch circuit protective device carries the current of more than one load. The tap conductors shall be sized to have an ampacity that is not less than 1/3 the ampacity of the branch circuit conductor, that carries the combined load current of the motor group, in accordance with 31.4.3.  Non-motor loads connected to a motor group shall be provided with an additional branch circuit protective device that complies with 31.4.4, 31.5 – 31.8, unless the branch circuit protection for the motor group meets these requirements.

L43 Feeder Taps for Motor Loads: Feeder tap conductors shall have an ampacity not less than that required by 29.6.1 and shall terminate in a branch-circuit protective device.

- Tap conductors no more than 10 feet in length shall be completely enclosed within the panel.

- Tap conductors no more than 25 feet in length shall be completely enclosed within the panel and have an ampacity of at least one-third that of the feeder conductors, or have an ampacity not less than the feeder conductors.

L44 Overcurrent Protection of Feeder: Any overcurrent protective devices located on the line side of branch circuit protection shall comply with the requirements in Section 32.

L45 Load Controllers: Each load switching device, whether operated by manual or automatic means, shall comply with Section 33 for the load type as in Table 33.1 and output load rating established by the manufacturer.

L46 Motor Overload Protection: Each motor circuit shall have provisions for overload protection in accordance with 34.3.1. Motor overload protection provided as a part of an industrial control panel shall comply with the requirements in Section 34.

L47 Power Transformer: When provided in an industrial control panel, a power transformer, as defined in 2.42 and Figure 6.1, shall comply with section 35.

# CONTROL CIRCUITS

L48 General: Each industrial control panel provided with one or more components that are only involved in controlling the operation of loads but not the load current itself shall comply with the requirements in Sections 37-48. A component that carries current for both a power circuit component and a control circuit component shall comply with the requirements for power circuits.

L49 Field Wiring: All panels are required to comply with Section 37 for all electrical connections to a separate control circuit power supply input, and all input and output control devices located outside of the panel.

L50 Internal Wiring: All panels are required to comply with Section 38 for all factory provided electrical connections between components provided as part of the panel. Control circuit wire size is determined according to 38.2.1 for the minimum control circuit conductor allowed unless additional overcurrent protection is provided as in 40.2.2.  Unless otherwise described in the Procedure, printed wiring boards used for factory connections between components of a control circuit shall be an integral part of a Listed or Recognized Component, or shall be installed in a circuit that complies with the requirements in Section 43, Section 44 or Appendix B.

L51 Conductor Sizing Greater Than 10 Amps: Paragraph 38.2.1(b)(1) requires Table 28.1 to be used for control circuit internal wiring ampacities for 14AWG and larger conductors.

L52 Overcurrent Protection: A control circuit shall have overcurrent protection that complies with 40.2 except as in 40.3.2(b) and 40.3.2(c).

L53 Overcurrent Protection for Grounded Conductor: Overcurrent protection shall be provided in each ungrounded conductor as in 40.2.1 and 40.2.2. An overcurrent protector may be provided in a grounded conductor if the ungrounded conductor is opened simultaneously with the grounded conductor.

L54 Switching Devices: A control circuit switching device shall comply with the requirements in Section 45 and shall be suitably rated for the control circuit load(s) controlled, see section 46.

L55 Loads: A control circuit load shall comply with the requirements contained in Section 46.

# RATINGS

L56 General: Each industrial control panel shall be assigned electrical ratings for every input and output circuit in accordance with Sections 49 – 51. The maximum voltage rating for a source of supply to the panel is 1000V.

L57 Short Circuit Current Ratings: All industrial control panels containing a power circuit are required to have a short circuit current rating included as part of the electrical ratings for each input to a power circuit in accordance with the requirements in 49.5, 76.3, Supplement SB and any additional information contained in the Procedure. An industrial control panel that contains only control circuits is not required to have a short circuit current rating. No other short circuit current ratings shall be included on the industrial control panel nameplate unless otherwise described in the Standard or the Procedure.

L58 Combination Motor Controllers: Combination motor controllers whose construction and ratings can be verified from the latest information available from the UL website, “ http://industries.ul.com/industrial-systems-and-components/industrial-control-products-and-systems/short-circuit-current-ratings-for-combination-motor-controller-components”, may be utilized in Listed industrial control panels and are not required to be described in the Procedure. The short circuit current rating corresponding to a specific combination motor controller is considered to apply for the assembly, regardless of the individual component short circuit current ratings only when:

- All the Listed or Recognized components specified are provided as part of the industrial control panel;

- All conditions of use stipulated in the database for the specific combination are met; and

- The assembly complies with all applicable UL508A construction requirements including internal conductor size, spacings, ratings, and markings.

L59 Series Connected Circuit Breakers: Short circuit current ratings based on the Recognized component series-connected device category (DKSY2), either manufacturers let-through data, or short circuit test results documented in UL letter reports (only), shall not be used to determine short circuit current ratings of industrial control panels unless specific construction details are described in the Procedure.

L60 Maximum Ambient Temperature: 40o C maximum, unless otherwise specified in the Procedure.

L61 Maximum Pneumatic Pressure Rating: 300 psi maximum, compressed air, in accordance with Section 48, unless otherwise specified in this Procedure.

# MARKINGS

L62 General: Each industrial control panel shall be marked in accordance with Sections 52 – 61. Table 52.1 identifies the location of each required marking with regard to whether the panel is an enclosed or an open-type panel.  A dash in the column for open type panels means the corresponding marking requirement does not apply to an open industrial control panel.

L63  Field Provided Components:

An industrial control panel schematic wiring diagram that includes devices that are not provided with the industrial control panel shall be marked to indicate that these devices shall be provided by the installer. Components listed as field installed on the wiring schematic shall

- Meet the components requirements for both Listed and Recognized components as described in the Supplement SA (not intended to circumvent or replace the component requirements in UL 508A).

- Include Manufacturers name, model number, applicable certification(s) required and installation instructions on the field wiring diagram, prints, or instructions that are referenced on the panel nameplate and shipped with the panel.

L64 Enclosure Type Rating: The enclosure type rating of an enclosed industrial control panel shall be included on the panel nameplate along with other ratings established by the panel manufacturer.  The Type ratings marked by the manufacturer of the enclosure shall not be modified, when the manufacturer of the enclosure is not the same as the manufacturer of the complete enclosed industrial control panel.

L65 Schematic Wiring Diagram: An industrial control panel and any schematic wiring diagrams or drawings provided with the panel shall not be marked with information pertaining to a hazardous (classified) location, such as Class, Division, Group or Zone, followed by a number or letter.

L66 Hazardous Locations: An industrial control panel and any schematic wiring diagrams or drawings provided with the panel shall not refer to low voltage outputs, Class 2 outputs, or intrinsically safe outputs for field connection to circuits extending into a hazardous (classified) location, such as Class, Division, Group or Zone followed by numbers and/or letters.

L67 Fountain Control Panels: An industrial control panel, including a fountain control panel, and any schematic wiring diagrams or drawings provided with the panel shall not be marked with information pertaining to use with swimming pools, spas, water-play fountains, water-play areas and fountains with water in common with swimming pools and shall not contain low voltage or class 2 outputs for connection to field installed conductors supplying wet-niche or no-niche lighting fixtures.

L68 Gas Detection Panels: An industrial control panel and any schematic wiring diagrams or drawings provided with the panel shall not be marked with information pertaining to use with or connections to smoke detectors, fire alarms, central station alarms, gas or vapor detection sensors or initiating devices.

L69 Access Control Systems: An industrial control panel and any schematic wiring diagrams or drawings provided with the panel shall not be marked with information pertaining to access control systems or connections to access control or security related peripheral components or systems, such as inputs from key or card-reader / key-pad access / biometric identification (fingerprint)/ security loop / motion detector, outputs to electrically-operated door locking devices, door operators and / or security doors, references to input or output devices provided in burglary-resistant enclosures, or contain low voltage circuits for closed circuit television surveillance, burglar alarms or central station alarms.  This does not apply to peripheral input signals or output door-locking devices or circuits that are marked as machine safeguarding devices whose operation stops, or prevents start-up, of a machine, or serves to lock guards or doors providing protection from hazardous electrical and/or moving machine parts.

# SPECIFIC USE INDUSTRIAL CONTROL PANELS

L70 General: The Field Engineer shall confirm that Industrial Control Panels marked for a specific use  comply with applicable specific use requirements in Part 2 (Sections 65-114) of the Standard or as described in the Procedure. The Part 2 requirements are used in addition to the requirements for enclosed or open industrial control panels in L11 – L69.

L71 Service Equipment: Industrial control panels marked for service equipment use shall comply with the requirements in Sections 73 - 79.

L72 Reserved.

L73 Flame Control: Industrial control panels marked for flame control that contain a primary safety control (see 81.2), an ignition transformer (see 81.3), or both, shall comply with the requirements in Sections 81 – 83.

L74 Fountain Control: Industrial control panels marked for permanently installed fountains or floating fountains shall comply with the requirements in Sections 93 – 96.

L75 Crane or Hoist Control: Industrial control panels marked as crane or hoist control shall comply with the requirements in Sections 68 - 72.

L76 Air Conditioning and/or Refrigeration Control: Industrial control panels marked for use with air conditioning and/or refrigeration equipment shall comply with the requirements in Sections 88 - 92.

L77 Marine Use: Industrial control panels marked for marine use shall comply with the requirements in Sections 84 - 87.

L78 Industrial Machinery: Industrial control panels marked for use with industrial machinery will need to comply with the requirements in Sections 65 - 67. The following are significant changes in the requirements in these Sections:

66.1.1 - Requires 110 degrees of minimum travel for swing out panels.

66.1.2 - Requires enclosure doors to be interlocked with the disconnecting means such that all doors are prevented from opening when the disconnect switch is in the “on” position.

66.1.4 - Requires internal maintenance lighting circuits and external work light circuits to be protected by 15A maximum branch circuit protective device.

66.1.5 - Requires minimum number of screw threads into sub-panel and for components mounted to fixed sub-panels so they can be removed without removing the sub-panel.

66.2.1 - Requires the physical arrangement of all control circuit components, regardless of voltage, to be grouped or mounted separately from all power circuit components.

66.2.2 - Requires grouping, separation or color coding of field wiring terminals of power circuits, control circuits, and externally supplied control circuits (yellow wire).

66.3.2 - Requires control transformer secondary circuits that are not grounded to be provided with ground detection means.

66.3.4 - Requires a factory supplied bonding conductor between the control panel enclosure and a door containing electrical components operating at more than 30Vrms.

66.6.1 - Allows only terminals to be provided on the line side of the disconnecting means. Other components cannot be installed on the line side of the disconnecting means unless identified in the Exception.

66.6.3 - Requires the disconnecting means to be readily accessible, and lockable in the “off” position independent of the position of the enclosure door.

66.8.1 - Requires both mechanical and electrical interlocking for contactors of wye-delta controllers.

66.8.3 - Requires robot controllers to be Listed and the panel or installation diagram to be marked with the designated Listed manipulator arm to be installed in the field.

66.11.3 - Requires emergency stop emergency stop buttons or actuators and the associated contact blocks shall comply with the requirements in the Standard for “Low-voltage Switchgear and Controlgear – Part 5-5: Control Circuit Devices and Switching Elements – Electrical Emergency Stop Device with Mechanical Latching Function”, UL 60947-5-5. Compliance is verified when Listed emergency stop devices (UL CCN: NISD) are used.

67.1.1 – Requires panel nameplate electrical ratings to include the ampere rating of the largest heater load.

L79 Aquatic Playground Control: Industrial control panels marked for Aquatic playgrounds shall comply with the requirements in Sections 100 - 104.

L80 Swimming Pool Control: Industrial control panels marked for swimming pool and in-ground spas shall comply with the requirements in Sections 105 - 109.

L81 Water Park Ride Control: Industrial control panels marked for water park rides and similar installations shall comply with the requirements in Sections 110 - 114.

L82 Irrigation Control: Industrial control panels marked for irrigation control shall comply with the requirements in Sections 97 - 99.

# MANUFACTURER’S TEST PROGRAM

L83 General: The tests described in Table L3 are required to be conducted by the manufacturer on 100% production in accordance with UL 508A:

TABLE L3

| Paragraph | Test Name | Additional Notes |
| --- | --- | --- |
| 79.1 | Ground Fault Protection Test | a) Required only when the control panel is additionally marked “Suitable for use as service equipment” b) The results of tests performed to Section 79 shall be included with installation instructions as described in 78.1(e). |
| B3.2 | Ground Fault Circuit Interrupter Functional Test | a) Required only when a component not previously investigated by UL is installed in accordance with Appendix B. b) The test records of tests performed to Section B3 shall be complete, as described in B3.3. |

L84 Pass/Fail: The Field Engineer shall review the Procedure for testing the product and shall verify that all product intended for labeling is tested, that nonconforming products are segregated, repaired, and re-tested before they are labeled, and that the testing equipment is in good condition.